## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Bsh | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 3703.0375 | 0 | 3703.0375 | 133.3093 | 0 | 133.3093 | 0.30688 | 100 | 2.0257 | 0 | 120.6667 | 1 | 2896 | 3703.0375 | 0 | 3703.0375 | 0 | 0
Bsh | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 3060.7656 | 0 | 3060.7656 | 110.1876 | 0 | 110.1876 | 0.25365 | 100 | 1.1196 | 0 | 120.6667 | 1 | 2896 | 3060.7656 | 0 | 3060.7656 | -642.2719 | 17.3445
Bsh | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 4075.0262 | 0 | 4075.0262 | 146.7009 | 0 | 146.7009 | 0.33771 | 100 | 2.3233 | 0 | 120.6667 | 1 | 2896 | 4075.0262 | 0 | 4075.0262 | 371.9887 | -10.0455