## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Bwh | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 2696.811 | 42.8051 | 2739.6161 | 97.0852 | 1.541 | 98.6262 | 0.22704 | 100 | 2.5492 | 0.47438 | 120.6667 | 1 | 2896 | 2696.811 | 42.8051 | 2739.6161 | 0 | 0
Bwh | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 1956.9498 | 43.5211 | 2000.4709 | 70.4502 | 1.5668 | 72.017 | 0.16578 | 100 | 2.0571 | 0.47704 | 120.6667 | 1 | 2896 | 1956.9498 | 43.5211 | 2000.4709 | -739.1452 | 26.9799
Bwh | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 3103.8637 | 43.5211 | 3147.3848 | 111.7391 | 1.5668 | 113.3059 | 0.26083 | 100 | 2.7909 | 0.47704 | 120.6667 | 1 | 2896 | 3103.8637 | 43.5211 | 3147.3848 | 407.7687 | -14.8842