## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Chongqing | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 1860.5346 | 568.862 | 2429.3966 | 66.9792 | 20.479 | 87.4583 | 0.20133 | 100 | 3.3601 | 1.057 | 120.6667 | 1 | 2896 | 1860.5346 | 568.862 | 2429.3966 | 0 | 0
Chongqing | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 1056.0274 | 669.8123 | 1725.8397 | 38.017 | 24.1132 | 62.1302 | 0.14303 | 100 | 1.5953 | 1.0594 | 120.6667 | 1 | 2896 | 1056.0274 | 669.8123 | 1725.8397 | -703.5569 | 28.9602
Chongqing | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 2256.1654 | 549.0656 | 2805.231 | 81.222 | 19.7664 | 100.9883 | 0.23248 | 100 | 3.4791 | 1.0594 | 120.6667 | 1 | 2896 | 2256.1654 | 549.0656 | 2805.231 | 375.8344 | -15.4703