## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Dfd | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 4.486 | 37765.3692 | 37769.8552 | 0.16149 | 1359.5533 | 1359.7148 | 3.1301 | 100 | 0.32422 | 9.0229 | 120.6667 | 1 | 2896 | 4.486 | 37765.3692 | 37769.8552 | 0 | 0
Dfd | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 0 | 38851.4305 | 38851.4305 | 0 | 1398.6515 | 1398.6515 | 3.2197 | 100 | 0 | 9.0229 | 120.6667 | 1 | 2896 | 0 | 38851.4305 | 38851.4305 | 1081.5753 | -2.8636
Dfd | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 45.8611 | 37265.2872 | 37311.1483 | 1.651 | 1341.5503 | 1343.2013 | 3.0921 | 100 | 0.75824 | 9.0229 | 120.6667 | 1 | 2896 | 45.8611 | 37265.2872 | 37311.1483 | -458.7069 | 1.2145