## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Hebei Province | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 1461.2063 | 4690.5045 | 6151.7108 | 52.6034 | 168.8582 | 221.4616 | 0.50981 | 100 | 3.126 | 3.0608 | 120.6667 | 1 | 2896 | 1461.2063 | 4690.5045 | 6151.7108 | 0 | 0
Hebei Province | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 535.1109 | 5373.4028 | 5908.5137 | 19.264 | 193.4425 | 212.7065 | 0.48966 | 100 | 1.4242 | 3.0666 | 120.6667 | 1 | 2896 | 535.1109 | 5373.4028 | 5908.5137 | -243.1971 | 3.9533
Hebei Province | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 1979.8174 | 4492.447 | 6472.2645 | 71.2734 | 161.7281 | 233.0015 | 0.53638 | 100 | 3.266 | 3.0666 | 120.6667 | 1 | 2896 | 1979.8174 | 4492.447 | 6472.2645 | 320.5537 | -5.2108