## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Hunan Province | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 1461.287 | 1319.6285 | 2780.9154 | 52.6063 | 47.5066 | 100.113 | 0.23046 | 100 | 2.099 | 1.5489 | 120.6667 | 1 | 2896 | 1461.287 | 1319.6285 | 2780.9154 | 0 | 0
Hunan Province | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 953.583 | 1535.8139 | 2489.397 | 34.329 | 55.2893 | 89.6183 | 0.2063 | 100 | 1.3959 | 1.5538 | 120.6667 | 1 | 2896 | 953.583 | 1535.8139 | 2489.397 | -291.5185 | 10.4828
Hunan Province | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 1765.1672 | 1261.3561 | 3026.5233 | 63.546 | 45.4088 | 108.9548 | 0.25082 | 100 | 2.4301 | 1.5538 | 120.6667 | 1 | 2896 | 1765.1672 | 1261.3561 | 3026.5233 | 245.6079 | -8.8319