## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Jilin Province | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 449.3222 | 16748.1604 | 17197.4826 | 16.1756 | 602.9338 | 619.1094 | 1.4252 | 100 | 2.4398 | 5.3835 | 120.6667 | 1 | 2896 | 449.3222 | 16748.1604 | 17197.4826 | 0 | 0
Jilin Province | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 37.3747 | 18051.0938 | 18088.4685 | 1.3455 | 649.8394 | 651.1849 | 1.499 | 100 | 0.78805 | 5.3893 | 120.6667 | 1 | 2896 | 37.3747 | 18051.0938 | 18088.4685 | 890.9859 | -5.1809
Jilin Province | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 770.2413 | 16073.9065 | 16844.1478 | 27.7287 | 578.6606 | 606.3893 | 1.3959 | 100 | 2.8805 | 5.3893 | 120.6667 | 1 | 2896 | 770.2413 | 16073.9065 | 16844.1478 | -353.3348 | 2.0546