## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Macao | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 2829.001 | 3.7991 | 2832.8001 | 101.844 | 0.13677 | 101.9808 | 0.23476 | 100 | 1.9147 | 0.24121 | 120.6667 | 1 | 2896 | 2829.001 | 3.7991 | 2832.8001 | 0 | 0
Macao | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 2235.691 | 3.8317 | 2239.5227 | 80.4849 | 0.13794 | 80.6228 | 0.1856 | 100 | 1.2866 | 0.24248 | 120.6667 | 1 | 2896 | 2235.691 | 3.8317 | 2239.5227 | -593.2774 | 20.9431
Macao | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 3157.0234 | 3.8317 | 3160.8551 | 113.6528 | 0.13794 | 113.7908 | 0.26195 | 100 | 2.2624 | 0.24248 | 120.6667 | 1 | 2896 | 3157.0234 | 3.8317 | 3160.8551 | 328.055 | -11.5806