## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Shanghai | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 1026.4077 | 1999.7633 | 3026.171 | 36.9507 | 71.9915 | 108.9422 | 0.25079 | 100 | 1.9726 | 2.3937 | 120.6667 | 1 | 2896 | 1026.4077 | 1999.7633 | 3026.171 | 0 | 0
Shanghai | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 613.2095 | 2279.4307 | 2892.6401 | 22.0755 | 82.0595 | 104.135 | 0.23972 | 100 | 1.273 | 2.3956 | 120.6667 | 1 | 2896 | 613.2095 | 2279.4307 | 2892.6401 | -133.5308 | 4.4125
Shanghai | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 1285.4129 | 1920.4138 | 3205.8267 | 46.2749 | 69.1349 | 115.4098 | 0.26568 | 100 | 2.3081 | 2.3956 | 120.6667 | 1 | 2896 | 1285.4129 | 1920.4138 | 3205.8267 | 179.6557 | -5.9367