## Sheet1
EPW | Scenario | Desc | Wall_Alpha | Wall_Eps | Wall_Lambda_WmK | Roof_Alpha | Roof_Eps | Roof_Lambda_WmK | Total_Cooling_Energy_kWh | Total_Heating_Energy_kWh | Total_HVAC_Energy_kWh | Total_Cooling_MJ_per_m2 | Total_Heating_MJ_per_m2 | Total_HVAC_MJ_per_m2 | Daily_HVAC_kWh_per_m2 | Floor_Area_m2 | Peak_Cooling_Load_kW | Peak_Heating_Load_kW | Simulation_Days | Sampling_Scale | Raw_Total_Hours | Raw_Total_Cooling_Energy_kWh | Raw_Total_Heating_Energy_kWh | Raw_Total_HVAC_Energy_kWh | Delta_Energy_kWh | Saving_%
Sichuan | 对比基准 | 默认建筑材料（墙α≈0.6, ε≈0.9；屋面α≈0.7, ε≈0.9） | 0.6 | 0.9 | 0.6 | 0.7 | 0.9 | 0.2 | 1044.2463 | 1095.6429 | 2139.8892 | 37.5929 | 39.4431 | 77.036 | 0.17734 | 100 | 1.9314 | 1.5136 | 120.6667 | 1 | 2896 | 1044.2463 | 1095.6429 | 2139.8892 | 0 | 0
Sichuan | 辐射制冷 | 高反射、高发射率材料（如 α=0.1, ε=0.95） | 0.1 | 0.95 | 0.6 | 0.1 | 0.95 | 0.2 | 510.6669 | 1320.5605 | 1831.2275 | 18.384 | 47.5402 | 65.9242 | 0.15176 | 100 | 0.99295 | 1.5189 | 120.6667 | 1 | 2896 | 510.6669 | 1320.5605 | 1831.2275 | -308.6617 | 14.4242
Sichuan | 辐射制热/保温 | 高吸收、高发射率材料（如 α=0.9, ε=0.95） | 0.9 | 0.95 | 0.6 | 0.9 | 0.95 | 0.2 | 1391.1958 | 1056.9719 | 2448.1677 | 50.083 | 38.051 | 88.134 | 0.20289 | 100 | 2.389 | 1.5189 | 120.6667 | 1 | 2896 | 1391.1958 | 1056.9719 | 2448.1677 | 308.2786 | -14.4063